MODBUS RS485 Communication protocol

1、The communication adopts RS485 bus, with asynchronous serial signals having 1 start bit, 8 data bits, 1 end bit, no parity check, and a baud rate of 9600bps.

2、Compliant with standard MODBUS RTU protocol, 16 bit data structure, 16 bit CRC check low byte before high byte after.

4、The upper computer is the calling host, and the controller is the slave machine。

5、The master-slave communication uses three commands：

Command 03H (query 1 or more registers)

Send command: [Device address]+[Command number 03H]+[Start register address high 8 bits]+[Low 8 bits]+[Read register number high 8 bits]+[Low 8 bits]+[CRC check low 8 bits]+[CRC check high 8 bits]

Device response: [Device address]+[Command number 03H]+[Number of bytes returned]+[Data 1]+[Data 2]++ [Data n]+[Low 8 bits of CRC check]+[High 8 bits of CRC check]

Command 06H (Modify Single Register)

Send command: [Device address]+[Command number 06H]+[Register address to be set high 8 bits]+[Low 8 bits]+[Data to be set high 8 bits]+[Low 8 bits]+[CRC check low 8 bits]+[CRC check high 8 bits]

Device response: If the command sent by the computer is successfully returned intact, otherwise it will not respond

Command 10H (Modify Multiple Registers)

Send command: [Device address]+[Command number 10H]+[Start register address high 8 bits]+[Low 8 bits]+[Register number high 8 bits]+[Low 8 bits]+[Register byte number]+[Data 1 high 8 bits]+[Low 8 bits]++ [Data N high 8 bits]+[low 8 bits]+[CRC check low 8 bits]+[CRC check high 8 bits]

Device response: [Device address]+[Command number 10H]+[Start register address high 8 bits]+[Low 8 bits]+[Register number high 8 bits]+[Low 8 bits]+[CRC check low 8 bits]+[CRC check high 8 bits]

Parameter address (R indicates that the parameter is read-only, RW indicates that the parameter is readable and writable)

| data address | Description | set range | Remarks |
| --- | --- | --- | --- |
| R 0x0000 | Reserve |  |  |
| R 0x0001 | Reserve |  |  |
| R 0x0002 | Switch |  |  |
| R 0x0003 | Work status flag |  |  |
| R 0x0004 | Output flag 1 |  |  |
| R 0x0005 | Output Flag 2 |  |  |
| R 0x0006 | Output flag 3 |  |  |
| R 0x0007 | Fault flag 1 |  |  |
| R 0x0008 | Fault flag 2 |  |  |
| R 0x0009 | Fault flag 3 |  |  |
| R 0x000A | Fault flag 4 |  |  |
| R 0x000B | Fault flag 5 |  |  |
| R 0x000C | Fault flag 6 |  |  |
| R 0x000D | Fault flag 7 |  |  |
| R 0x000E | reserve |  |  |
| R 0x000F | Inlet water temperature | -30~99℃ |  |
| R 0x0010 | Outlet water temperature | -30~99℃ |  |
| R 0x0011 | Ambient temperature | -30~99℃ |  |
| R 0x0012 | Coil 1 temperature | -30~99℃ |  |
| R 0x0013 | Return gas 1 temperature | -30~99℃ |  |
| R 0x0014 | Cooling coil 1 temperature | -30~99℃ |  |
| R 0x0015 | Exhaust 1 temperature | 0~125℃ |  |
| R 0x0016 | Reserve |  |  |
| R 0x0017 | Reserve |  |  |
| R 0x0018 | Main expansion valve opening1 |  |  |
| R 0x0019 | Auxiliary expansion valve opening1 |  |  |
| R 0x001A | Compressor 1 target frequency |  |  |
| R 0x001B | Actual frequency of compressor 1 |  |  |
| R 0x001C | Frequency module 1 fault 1 |  |  |
| R 0x001D | Frequency module 1 fault 2 |  |  |
| R 0x001E | DC bus voltage value1 |  |  |
| R 0x001F | Heat sink temperature1 |  |  |
| R 0x0020 | Compressor phase current1 |  |  |
| R 0x0021 | Reserve |  |  |
| R 0x0022 | Reserve |  |  |
| R 0x0023 | Reserve |  |  |
| R 0x0024 | DC fan 1 speed |  |  |
| R 0x0025 | DC fan 2 speed (reserved) |  |  |
| R 0x0026 | Coil 2 temperature (reserved) | -30~99℃ |  |
| R 0x0027 | Return gas 2 temperature (reserved) | -30~99℃ |  |
| R 0x0028 | Refrigeration coil 2 temperature (reserved) | -30~99℃ |  |
| R 0x0029 | Exhaust 2 temperature (reserved) | 0~125℃ |  |
| R 0x002A | Reserve |  |  |
| R 0x002B | Reserve |  |  |
| R 0x002C | Main expansion valve opening 2 (reserved) |  |  |
| R 0x002D | Auxiliary expansion valve opening 2 (reserved) |  |  |
| R 0x002E | Target frequency of compressor 2 (reserved) |  |  |
| R 0x002F | Actual frequency of compressor 2 (reserved) |  |  |
| R 0x0030 | Frequency module 2 fault 1 (reserved) |  |  |
| R 0x0031 | frequency module 2 fault 2 (reserved)(reserved) |  |  |
| R 0x0032 | DC bus voltage value 2 (reserved) |  |  |
| R 0x0033 | Heat sink temperature 2 (reserved) |  |  |
| R 0x0034 | Compressor phase current 2 (reserved) |  |  |
| R 0x0035 | Reserve |  |  |
| R 0x0036 | Reserve |  |  |
| R 0x0037 | Reserve |  |  |
| R 0x0038 | Reserve |  |  |
| R 0x0039 | Reserve |  |  |
| R 0x003A | Total current of the unit |  |  |
| R 0x003B | Reserve |  |  |
| R 0x003C | Reserve |  |  |
| R 0x003D | Reserve |  |  |
| R 0x003E | Reserve |  |  |
| RW 0x003F | Parameter Flag Definition |  |  |
| RW 0x0040 | Mode |  |  |
| RW 0x0041 | Heating sett temperature | 8℃~40℃ |  |
| RW 0x0042 | Cooling set temperature | 8℃~28℃ |  |
| RW 0x0043 | Manual frequency setting |  |  |
| RW 0x0044 | Manual steps of expansion valve | 20~450 |  |
| RW 0x0045 | Manual steps of auxiliary valve |  |  |
| RW 0x0046 | Manual frequency setting 2 (reserved) |  |  |
| RW 0x0047 | Manual steps for expansion valve 2 (reserved) |  |  |
| RW 0x0048 | Auxiliary valve 2 manual steps (reserved) |  |  |
| RW 0x0049 | Manual wind speed |  |  |
| RW 0x004A | Reserve |  |  |
| RW 0x004B | Reserve |  |  |
| RW 0x004C | Reserve |  |  |

Control switch port

bit  0 : Reserve

bit  1 : Water flow switch

bit  2 : Low pressure switch

bit  3 :High pressure switch

bit  4 : Reserve

bit  5 : Reserve

bit  6 : Reserve

bit  7 : Emergency switch

Work status flag

bit  0 : Hot water available

bit  1 : High temperature

bit  2 : Heating

bit  3 : Cooling

bit  4 : Reserve

bit  5 : High water level

bit  6 : Low water level

bit  7 : Defrost

Output Flag

bit  0 : Compressor1

bit  1 : Compressor2（Reserve）

bit  2 : Reserve

bit  3 : Reserve

bit  4 : Reserve

bit  5 : Fan motor

bit  6 : Four-way valve

bit  7 : AC high and low wind 0=low wind/1=high wind

Output Flag 2

bit  0 : Reserve

bit  1 : Reserve

bit  2 : Reserve

bit  3 : Makeup valve

bit  4 : Reserve

bit  5 : Reserve

bit  6 : Air conditioning cooling demand

bit  7 : Air conditioning heating demand

Output flag 3

bit  0 : Reserve

bit  1 : Electric heating of crankshaft

bit  2 : Circulating water pump

bit  3 : Reserve

bit  4 : Reserve

bit  5 : Reserve

bit  6 : Reserve

bit  7 : Reserve

Fault flag 1

bit  0 : Reserve

bit  1 : Environmental temperature fault

bit  2 : Coil 1 temperature fault

bit  3 : Reserve

bit  4 : Water outlet temperature fault

bit  5 : High pressure Fault

bit  6 : Low pressure fault

bit  7 : Reserve

Fault Flag 2

bit  0 : Water flow switch failure

bit  1 : Reserve

bit  2 : Protection against excessive temperature of heating water outlet

bit  3 : Reserve

bit  4 : Reserve

bit  5 : Coil 2 temperature fault (reserved)

bit  6 : High pressure switch 2 fault (reserved)

bit  7 : Low voltage switch 2 fault (reserved)

Fault flag 3

bit  0 : Reserve

bit  1 : Reserve

bit  2 : Reserve

bit  3 : Reserve

bit  4 : Reserve

bit  5 : DC fan 2 fault (reserved)

bit  6 : Exhaust 1 temperature fault

bit  7 : Reserve

Fault flag 4

bit  0 : Inlet water temperature fault

bit  1 : Exhaust 1 temperature too high fault

bit  2 : Reserve

bit  3 : Reserve

bit  4 : Reserve

bit  5 : Cooling water outlet temperature supercooling protection

bit  6 : Suction air 1 temperature fault

bit  7 : Reserve

Fault flag 5

bit  0 : Reserve

bit  1 : Reserve

bit  2 : Coil 1 over temperature protection

bit  3 : Cooling coil 1 temperature fault

bit  4 : Reserve

bit  5 : Coil 2 over temperature protection (reserved)

bit  6 : Exhaust 2 temperature too high fault (reserved)

bit  7 : Reserve

Fault flag 6

bit  0 : Reserve

bit  1 : Reserve

bit  2 : Reserve

bit  3 : Reserve

bit  4 : Secondary antifreeze

bit  5 : First level antifreeze

bit  6 : Reserve

bit  7 : Reserve

Fault flag 7

bit  0 : Temperature fault of refrigeration coil 2 (reserved)

bit  1 : Reserve

bit  2 : Communication failure of frequency conversion module 2 (reserved)

bit  3 : Return gas 2 temperature fault (reserved)

bit  4 : Communication failure of variable frequency module 1

bit  5 : Exhaust 2 temperature fault (reserved)

bit  6 : DC fan 1 fault

bit  7 : Reserve

Parameter Flag Definition 1

bit  0 : Wire controlled switch

bit  1 : Manual frequency

bit  2 : Expansion valve mode selection 0 manual/1 automatic

bit  3 : Reserve

bit  4 : Water pump working mode 0=non-stop/1=periodic operation

bit  5 : Refrigeration expansion valve working mode 0=environment/1=superheat

bit  6 : Mute mode 0=no mute/1=with mute

bit  7 : Reserve

bit  8 : Strong mode 0=no strong/1=strong (when silent mode is present, silent mode takes priority)

bit  11 : Commodity inspection mode 0=Press operates normally/1=Press starts quickly

bit  13 : Fan mode

bit  14 : Forced defrosting

bit  15 : Parameter reset 0 not reset/1 Parameter reset

Mode

bit  0 : Mode selection 1 heating/2 cooling/7 automatic

bit  1 : Reserve

bit  2 : Reserve

bit  3 : Reserve

bit  4 : Strong mode  0 no strong mode /1 strong mode（reserve）

bit  5 : Reserve

bit  6 : Reserve

bit  7 : Reserve